| Cherwell District Council Planning and Development Services Bodicote House White Post Road Bodicote Banbury OX15 4AA | Our ref: WA/2011/109141/01-L01 Your ref: 10/01491/REM Date: 01 February 2011 |
| --- | --- |

# Dear Ms Griffiths

DISCHARGE OF CONDITION 12 OF 06/00967/OUT FOR PARCEL KM2.

KM2 DEVELOPMENT SITE, KINGSMERE DEVELOPMENT, MIDDLETON STONEY ROAD, BICESTER, OXFORDSHIRE.

We have assessed the surface water drainage calculations for the 1 in 10 year storm events submitted with the email from Geoff Hibbert of Bovis Homes dated 21 January 2011.

The performance of the system during the 1 in 10 year event is acceptable, but from a flood risk perspective the submitted details do not meet the requirements of Condition 12 at this time for the following reasons.

Although the design code only specifies a requirement for local SUDS to accommodate the 10 year storm event, maximum discharge rates are detailed elsewhere for the 1 in 30 year and 1 in 100 year (with an allowance for climate change) events.

It is therefore important to check the surface water drainage system will adhere to these specified discharge rates whilst meeting the requirements of PPS 25:

- No flooding of the system during storm events up to and including the 1 in 30 year storm event.

- Any flooding of the system during storm events up to and including the 1 in 100 year event with an allowance for climate change can be safely contained on the site (ideally there should be no flooding).

If you have any questions please don’t hesitate to contact me.

# Yours sincerely

Ms Michelle Kidd

Planning Liaison Officer

# Direct dial 01491 828455

Direct fax 01491 834703

Direct e-mail michelle.kidd@environment-agency.gov.uk

cc Bovis Homes Ltd