From: Hunt, Gordon - Environment & Economy - Highways & Transport [mailto:Gordon.Hunt@Oxfordshire.gov.uk] 
Sent: 03 June 2011 14:58
To: Planning
Cc: Keable, David - Environment & Economy - Highways & Transport
Subject: Whitelands Farm - South West Bicester -11/00565/CDC

Ftao Linda Griffiths

I am sorry for the delay in replying, my concerns are as follows:-

- No soakage test results

- Details of the pond sizing

- No flap valves on the pipe outfalls

- No filter membrane round the filter drain material (stops the silt blocking the voids between the stones)

From the information supplied I have no idea whether or not the pond will cope with the water flows or it will back up the ditches and silt up the pipes

Regards

Gordon Hunt

County Drainage Engineer