| Mr Kevin McEvaddy R P S Design Noble House Capital Drive Linford Wood Milton Keynes MK14 6QP | Our ref: WA/2013/116495/01-L01 Your ref: 13/00227/DISC Date: 13 December 2013 |
| --- | --- |

# Dear Mr McEvaddy

DISCHARGE OF CONDITION 12 (SURFACE WATER DRAINAGE REPORT)   KM7 & KM9 SOUTH WEST BICESTER DEVELOPMENT SITE MIDDLETON STONEY ROAD BICESTER OXFORDSHIRE

Thank you for consulting us on this matter. We received the letter on 27 November 2013 and we are now in a position to respond.

We note the submission by the applicant of the revised Surface Water Drainage Design Strategy for Kingsmere Parcels KM7 and KM9, Issue C, dated 26 November 2013.
 
Within this we can see that the applicant has provided the following:

- Calculations for the 1 in 10 year, 1 in 30 year and 1 in 100 year plus climate change events for parcels KM7 and KM9 to demonstrate where flooding occurs on the site during these events.

- A plan to show overland flows and flow routes to demonstrate where the water is going in parcels KM7 and KM9.

- Clarified the reference number for the Flow Control Chamber at Manhole S116.

- Clarified the flow restriction for KM7 as 13.8 l/s.

However there is insufficient information provided to be able to recommend discharge of condition 12 of 06/00967/OUT.
 
Additional information on the network drainage design will be required to discharge the surface water condition for these parcels of development. In particular:

- Plan JKK6647 SK02 B shows flooded volumes, flood flows and direction of overland flows but there is no commentary on what impact these would have on the site and whether these would cause a hazard. We require a commentary to explain the depths and velocities of the flood flows, what the impacts of these are, whether they cause a hazard and how they are safely contained.

- The flooded volumes in the two tables shown on Plan JKK6647 02B do not tie up with those in the Micro Drainage calculations provided and at least one of the storm durations does not tie up with those in the calculations. We require the applicant to check the figures in the two tables and include the correct figures or explain why the figures included are correct.

# Yours sincerely,

Mr Jack Moeran

Planning Advisor

# Direct dial 01491 828367

Direct e-mail planning-wallingford@environment-agency.gov.uk