| Cherwell District Council Planning & Development Services Bodicote House White Post Road Bodicote Banbury OX15 4AA | Our ref: WA/2014/117162/02-L01 Your ref: 14/00221/REM Date: 21 July 2014 |
| --- | --- |

# Dear Ms Griffiths,

RESERVED MATTERS TO OUTLINE APPLICATION 06/00967/OUT - APPROVAL OF ALL RESERVED MATTERS FOR THE CONSTRUCTION OF 257 DWELLINGS ON LAND PARCELS KMC AND KMD.

KM15 KM16 AND KM18 SOUTH WEST BICESTER DEVELOPMENT SITE MIDDLETON STONEY ROAD BICESTER OXFORDSHIRE

Further to our letter of objection to you, dated 18 March 2014 we received further information in an email from Chris Brackley dated 30 June. We are now in a position to respond.

We maintain our objection on flood risk grounds. Further clarification on the following points is required.

- The report has stated that the porous paving will accommodate the 10 year storm event but it is not completely clear how this has been represented in the model. Has the infiltration aspect been discounted from the network calculations or have separate calculations been done which have not been submitted.

- The drainage calculations show that the duration of storm events only run to 1440 minutes. Good practice usually extends the duration to 7 days (10080 minutes). We would appreciate an explanation as to the justification for this.

- In the submitted statement it indicates that any roofed areas which cannot be discharged to the permeable paving will be directed to rear garden soakaways. This would contribute to the overall runoff from the site and we need to understand how this split between public and private runoff is managed within the overall catchment. As part of this we would expect to see calculations for the private soakaways to show that they are able to infiltrate a range of storm events. We would also require a confirmation as to whether these soakaways have been designed to accommodate runoff from the 1 in 100, with an appropriate allowance for climate change, storm event.

# Yours sincerely,

Mr Jack Moeran

Planning Advisor

# Direct dial 01491 828367

Direct e-mail planning-wallingford@environment-agency.gov.uk

cc Mr Peter Haslam