##### Ventilation Details

PROJECT No:-	SSP 339			SITE NAME :-	RED LION

ENGINEER:-	D RICHARDS		ADDRESS :-		WENDLEBURY ROAD

BICESTER

DATE			10/6/2015						OX25 2PW

Extraction

6600  x  1500  x  500  Stainless Steel supply/extract canopy c/w  12  off  495x395x45 baffle type filters.

Ductwork extracts via pitched roof above.

Extract fan

Zeihl Abegg ZAC 560 cased axial fan unit 		Airflow  =   2.68M³/s @ 150 pa.

Motor Data

Start Current = 15A	FLC = 7.5A 	Rpm = 1300	kW = 1.6	dba @ 3M = 68

Controller - 	RTRE 7 Auto transformer

Air Input

Powered via externally roof mounted ductwork c/w fan unit and disposable G4 paper filter.

The supply section of the canopy will be installed with 3 off 1200 x 200 single diffuser grilles.

Supply fan

Soler & Palau HCBB / 4-500/H plate mounted axial fan unit 	Airflow  =   1.76M³/s @ 125 pa.

Motor Data

Current = 3A	kW = 0.65	Rpm = 1290	dba @ 3M = 68

Controller - 	RTRE 5 Auto transformer

Stainless Wall Cladding		Yes – underside of wall canopy.

Lights					Yes – 3 off  recessed fluorescent (see drawing details)

Gas Interlock Panel			Yes – S&S Northern CT 1250 c/w Emergency stop button.

Gas solenoid				Yes – Mounted within cook line manifold.