| Cherwell District Council Planning & Development Services Bodicote House White Post Road Bodicote Banbury OX15 4AA | Our ref: WA/2013/114375/01-L01 Your ref: 13/00321/OUT Date: 26 April 2013 |
| --- | --- |

# Dear Ms Bailey,

1000 DWELLINGS TOGETHER WITH A LOCAL CENTRE INCLUDING RETAIL (A1), FINANCIAL SERVICES (A2), RESTAURANTS (A3-A5), UP TO A COMBINED TOTAL FLOORSPACE OF 1000M2, EMPLOYMENT SPACE (B1) UP TO A TOTAL FLOORSPACE OF 5000M2 WITH THE B1(A) OFFICE COMPONENT LIMITED TO A MAXIMUM OF 2,500M2, ASSOCIATED CAR PARKING, A COMMUNITY PRIMARY SCHOOL (INCLUDING SPACE FOR COMMUNITY USES (D1) AND ASSEMBLY AND LEISURE USES (D2)), GREEN INFRASTRUCTURE INCLUDING FORMAL AND INFORMAL OPEN SPACE, AMENITY SPACE, RETAINED HEDGEROWS, STRUCTURAL LANDSCAPING, SUPPORTING INFRASTRUCTURE (INCLUDING GAS, ELECTRICITY, SEWERAGE, WATER, TELECOMMUNICATIONS), SUSTAINABLE URBAN DRAINAGE SYSTEMS, NEW CONNECTION TO THE A361 BLOXHAM ROAD, PEDESTRIAN AND CYCLING CONNECTIONS TO THE SURROUNDING FOOTPATH AND CYCLE NETWORK AND ANY NECESSARY DEMOLITION AND GROUND REMODELLING.

LAND INCLUDING OS7400, 5257, 4976, 2661, AND 5257 SOUTH OF SALT WAY ADJ TO BLOXHAM ROAD BANBURY

Thank you for consulting us on this matter. We received the letter on 11 March 2013 and we are now in a position to respond.

Environment Agency position

In the absence of an acceptable Flood Risk Assessment (FRA) we object to the grant of planning permission and recommend refusal on this basis for the following reasons:
 
Reason

The FRA submitted with this application does not comply with the requirements set out in paragraph 9 of the Technical Guide to the National Planning Policy Framework. The submitted FRA does not therefore, provide a suitable basis for assessment to be made of the flood risks arising from the proposed development.

In particular, the submitted FRA fails to:

- Demonstrate that the storage volume required to attenuate surface water run-off from the critical 1 in 100 chance in any year storm event, with an appropriate allowance for climate change, can be provided on site.

- Demonstrate that the peak discharge rate for all events up to and including the 1 in 100 chance in any year critical storm event, including an appropriate allowance for climate change, will not exceed pre-development Greenfield runoff rates.

Overcoming our objection

We consider the Qbar runoff rate of 0.15 litres/second/hectare to be extremely low. We are concerned about the use an erroneously low rate as a starting point, as it could lead to future problems with the design of the surface water attenuation system. It is possible that one of the design parameters is incorrect and we suggest the applicant checks the calculations

The applicant must demonstrate through their surface water strategy that the proposed development will not create an increased risk of flooding from surface water. Surface water for up to the 1 in 100 chance in any year storm event, including an allowance for climate change, must be safely contained on site. It may be acceptable for limited flooding to occur in parts of the site during this event, ensuring that buildings are not affected by flooding and the site can be safely navigated by users. Where this flooding will be within roads or pathways, the applicants must ensure that safe access and egress is still available.

The surface water strategy should be carried out in accordance with the National Planning Policy Framework and PPS25 Practice Guide giving preference to infiltration over discharge to a watercourse, which in turn is preferable to discharge to surface water sewer.

Guidance on the preparation of surface water strategies can be found in the Defra/Environment Agency publication "Preliminary rainfall runoff management for developments". Guidance on climate change allowances can be found within the National Planning Policy Framework Technical Guidance.

The applicant should, as part of the surface water strategy, demonstrate that the requirements of any local surface water drainage planning policies have been met and the recommendations of the relevant Strategic Flood Risk Assessment and Surface Water Management Plan have been considered.
 
The CIRIA publication ‘C635 Designing for exceedance in urban drainage— Good practice’ contains advice on surface water conveyance and storage. The document can be accessed at www.ciria.com/suds/ciria_publications.htm

Further information on SUDS can be found in:

- PPS25 Practice Guide.

- CIRIA C522 document Sustainable Drainage Systems – design manual for England and Wales.

- CIRIA C697 document SUDS manual.

# Yours sincerely,

Mr Jack Moeran

Planning Advisor

# Direct dial 01491 828367

Direct e-mail planning-wallingford@environment-agency.gov.uk

cc David Lock Associates Ltd.