Sent: 29 May 2015 14:34

To: Planning

Subject: 3rd Party Planning Application - 15/00837/OUT

Cherwell District Council                                             Our DTS Ref: 42649

Planning & Development Services                                       Your Ref: 15/00837/OUT

Bodicote House

Bodicote, Banbury

Oxon

OX15 4AA

29 May 2015

Dear Sir/Madam

Re: LAND ON THE NORTH EAST SIDE OF, GAVRAY DRIVE, BICESTER, OXFORDSHIRE, OX26

Waste Comments

Following initial investigation, Thames Water has identified an inability of the existing waste water infrastructure to accommodate the needs of this application. Should the Local Planning Authority look to approve the application, Thames Water would like the following 'Grampian Style' condition imposed. "Development shall not commence until a drainage strategy detailing any on and/or off site drainage works, has been submitted to and approved by, the local planning authority in consultation with the sewerage undertaker. No discharge of foul or surface water from the site shall be accepted into the public system until the drainage works referred to in the strategy have been completed". Reason - The development may lead to sewage flooding; to ensure that sufficient capacity is made available to cope with the new development; and in order to avoid adverse environmental impact upon the community. Should the Local Planning Authority consider the above recommendation is inappropriate or are unable to include it in the decision notice, it is important that the Local Planning Authority liaises with Thames Water Development Control Department (telephone 0203 577 9998) prior to the Planning Application approval.

Surface Water Drainage - With regard to surface water drainage it is the responsibility of a developer to make proper provision for drainage to ground, water courses or a suitable sewer. In respect of surface water it is recommended that the applicant should ensure that storm flows are attenuated or regulated into the receiving public network through on or off site storage. When it is proposed to connect to a combined public sewer, the site drainage should be separate and combined at the final manhole nearest the boundary. Connections are not permitted for the removal of groundwater. Where the developer proposes to discharge to a public sewer, prior approval from Thames Water Developer Services will be required. They can be contacted on 0800 009 3921. Reason - to ensure that the surface water discharge from the site shall not be detrimental to the existing sewerage system.

Water Comments

Thames Water recommend the following informative be attached to this planning permission. Thames Water will aim to provide customers with a minimum pressure of 10m head (approx 1 bar) and a flow rate of 9 litres/minute at the point where it leaves Thames Waters pipes.  The developer should take account of this minimum pressure in the design of the proposed development.

Supplementary Comments

The receiving public sewer may not have sufficient spare capacity to accommodate the anticipated net foul flow increase from the proposed development. Thames Water request that an impact study be undertaken to ascertain, with a greater degree of certainty, whether the proposed development will lead to overloading of existing infrastructure, and, if required, recommend network upgrades. The applicant is requested to contact Thames Water Developer Services on 0800 009 3921 at the earliest opportunity to progress an impact study.

Yours faithfully

Development Planning Department

Development Planning,

Thames Water,