# From: BCTAdmin@thameswater.co.uk [mailto:BCTAdmin@thameswater.co.uk]

Sent: 11 April 2014 13:41

To: Planning

Subject: 3rd Party Planning Application - 14/00412/F

Cherwell District Council                                             Our DTS Ref: 40306

Planning & Development Services                                       Your Ref: 14/00412/F

Bodicote House

Bodicote, Banbury

Oxon

OX15 4AA

11 April 2014

Dear Sir/Madam

Re: LAND ADJOINING AND WEST OF STONECROFT HOUSE, CLIFTON ROAD, DEDDINGTON, BANBURY, OXFORDSHIRE, OX15 0TP

Waste Comments

With the information provided Thames Water, has been unable to determine the waste water infrastructure needs of this application. Should the Local Planning Authority look to approve the application ahead of further information being provided, we request that the following 'Grampian Style' condition be applied - "Development shall not commence until a drainage strategy detailing any on and/or off site drainage works, has been submitted to and approved by, the local planning authority in consultation with the sewerage undertaker. No discharge of foul or surface water from the site shall be accepted into the public system until the drainage works referred to in the strategy have been completed". Reason - The development may lead to sewage flooding; to ensure that sufficient capacity is made available to cope with the new development; and in order to avoid adverse environmental impact upon the community. Should the Local Planning Authority consider the above recommendation is inappropriate or are unable to include it in the decision notice, it is important that the Local Planning Authority liaises with Thames Water Development Control Department (telephone 0203 577 9998) prior to the Planning Application approval.

Surface Water Drainage - With regard to surface water drainage it is the responsibility of a developer to make proper provision for drainage to ground, water courses or a suitable sewer. In respect of surface water it is recommended that the applicant should ensure that storm flows are attenuated or regulated into the receiving public network through on or off site storage. When it is proposed to connect to a combined public sewer, the site drainage should be separate and combined at the final manhole nearest the boundary. Connections are not permitted for the removal of groundwater. Where the developer proposes to discharge to a public sewer, prior approval from Thames Water Developer Services will be required. They can be contacted on 0845 850 2777. Reason - to ensure that the surface water discharge from the site shall not be detrimental to the existing sewerage system.

Thames Water would recommend that petrol / oil interceptors be fitted in all car parking/washing/repair facilities. Failure to enforce the effective use of petrol / oil interceptors could result in oil-polluted discharges entering local watercourses.

Water Comments

Thames Water recommend the following informative be attached to this planning permission. Thames Water will aim to provide customers with a minimum pressure of 10m head (approx 1 bar) and a flow rate of 9 litres/minute at the point where it leaves Thames Waters pipes.  The developer should take account of this minimum pressure in the design of the proposed development.

Supplementary Comments

Wastewater - confirmation of surface water disposal is required. Following initial investigation, Thames Water has identified an inability of the existing waste water infrastructure to accommodate surface water in the foul sewer. Where there are no Surface Water sewers connection of surface water to a Foul Sewer will only be considered when all other methods of disposing of the surface water have been proven impracticable. Where disposal of surface water is other than to a public sewer, then the applicant shall ensure that approval for the discharge has been obtained from the appropriate authorities. In accordance with the Building Act 2000 clause H3.3. Positive connection to a public surface water will only be consented when it can be demonstrated that the hierarchy of disposal methods have been examined and proven to be impracticable. The disposal hierarchy being ;- 1st Soakaways; 2nd Watercourses; 3rd Sewer. Discharges shall be attenuated to reduce the likelihood of flooding downstream of the point of connection. As a guide a discharge rate of 5 litres/second/Hectare will be use in most instances, however more onerous constraints may be imposed to fit local circumstances. The system shall not show signs of flooding above ground for the worst 1 in 30 year storm, and shall be tested for exceedance in a 1 in 100 year storm to demonstrate any flooding that may occur will not flood properties.

Yours faithfully

Development Planning Department

Development Planning,

Thames Water,

Maple Lodge STW,

Denham Way,

Rickmansworth,

WD3 9SQ