Sent: 01 September 2015 16:49

To: Planning

Subject: 3rd Party Planning Application - 15/00839/REM (Aug 15)

Cherwell District Council                                             Our DTS Ref: 46953

Planning & Development Services                                       Your Ref: 15/00839/REM (Aug 15)

Bodicote House

Bodicote, Banbury

Oxon

OX15 4AA

1 September 2015

Dear Sir/Madam

Re: LONGFORD PARK PARCEL D AND PHASE 3, LONGFORD PARK ROAD, BODICOTE, BANBURY, OXFORDSHIRE, OX15 4AB

Waste Comments

Following initial investigation, Thames Water has identified an inability of the existing waste water infrastructure to accommodate the needs of this application. Should the Local Planning Authority look to approve the application, Thames Water would like the following 'Grampian Style' condition imposed. "Development shall not commence until a drainage strategy detailing any on and/or off site drainage works, has been submitted to and approved by, the local planning authority in consultation with the sewerage undertaker. No discharge of foul or surface water from the site shall be accepted into the public system until the drainage works referred to in the strategy have been completed". Reason - The development may lead to sewage flooding; to ensure that sufficient capacity is made available to cope with the new development; and in order to avoid adverse environmental impact upon the community. Should the Local Planning Authority consider the above recommendation is inappropriate or are unable to include it in the decision notice, it is important that the Local Planning Authority liaises with Thames Water Development Control Department (telephone 0203 577 9998) prior to the Planning Application approval.

Water Comments

Supplementary Comments

Detailed discussions about the design and funding of the offsite drainage infrastructure to serve Longford Park development are still ongoing with the developer and Thames Water. Additional foul flows arising from this development are likely to lead to sewer flooding of properties without a long term drainage solution being put in place. We consider that the drawings ref 20488_02_070_10.1, 20488_02_070_10.2, 20488_02_070_10.3 and 20488_02_070_10.4, submitted as part of the reserved matters application do not address this issue.

The drainage report needs to include the following:

Foul flow - exact details and plans of how the sewers will connect to the strategic onsite foul network.

Foul flow - details of the offsite drainage measures to avoid the risk of sewer flooding to existing residents caused by the additional flows from the development.

Yours faithfully

Development Planning Department

Development Planning,

Thames Water,

Maple Lodge STW,

Denham Way,

Rickmansworth,

WD3 9SQ