# From: BCTAdmin@thameswater.co.uk [mailto:BCTAdmin@thameswater.co.uk]

Sent: 27 January 2015 15:20

To: Planning

Subject: 3rd Party Planning Application - 14/02156/OUT

Cherwell District Council                                             Our DTS Ref: 44186

Planning & Development Services                                       Your Ref: 14/02156/OUT

Bodicote House

Bodicote, Banbury

Oxon

OX15 4AA

27 January 2015

Dear Sir/Madam

Re: LAND SOUTH OF COTEFIELD BUSINESS PARK, OXFORD ROAD, BODICOTE, OXFORDSHIRE, OX15

Waste Comments

Following initial investigation, Thames Water has identified an inability of the existing waste water infrastructure to accommodate the needs of this application. Should the Local Planning Authority look to approve the application, Thames Water would like the following 'Grampian Style' condition imposed. “Development shall not commence until a drainage strategy detailing any on and/or off site drainage works, has been submitted to and approved by, the local planning authority in consultation with the sewerage undertaker. No discharge of foul or surface water from the site shall be accepted into the public system until the drainage works referred to in the strategy have been completed”. Reason - The development may lead to sewage flooding; to ensure that sufficient capacity is made available to cope with the new development; and in order to avoid adverse environmental impact upon the community. Should the Local Planning Authority consider the above recommendation is inappropriate or are unable to include it in the decision notice, it is important that the Local Planning Authority liaises with Thames Water Development Control Department (telephone 0203 577 9998) prior to the Planning Application approval.

Water Comments

Thames Water recommend the following informative be attached to any planning permission: There is a Thames Water main crossing the development site which may/will need to be diverted at the Developer’s cost, or necessitate amendments to the proposed development design so that the aforementioned main can be retained. Unrestricted access must be available at all times for maintenance and repair. Please contact Thames Water Developer Services, Contact Centre on Telephone No: 0800 009 3921 for further information.

Thames Water recommend the following informative be attached to this planning permission. Thames Water will aim to provide customers with a minimum pressure of 10m head (approx 1 bar) and a flow rate of 9 litres/minute at the point where it leaves Thames Waters pipes.  The developer should take account of this minimum pressure in the design of the proposed development.

Supplementary Comments

The receiving sewer may not have sufficient spare capacity to accommodate the calculated net foul flow increase from the proposed development. Thames Water request that an impact study be undertaken to ascertain, with a greater degree of certainty, whether the proposed development will lead to overloading of existing infrastructure, and, if required, recommend network upgrades. Please liaises with Thames Water Development Control Department (telephone 0845 850 2777) with regard to arranging an impact study.

Yours faithfully

Development Planning Department

Development Planning,

Thames Water,

Maple Lodge STW,

Denham Way,

Rickmansworth,

WD3 9SQ